## Sheet1
id | Product | Parts | Description | Reference | Risklevel | Photo | Dropdown | functional _point | Positive_MNT | Positive_ADJ | Negative_MNT | Negative_ADJ | Emergency_Features | Customer_Scope | MNT _ADJ | marks | security | dropdown_count | INF30_Key_Abstract_S_No
1 | LIFT | PIT | PIT IDENTIFICATION | When there are more than one lift in the building, pit identification should be provided in all lifts | 3~3~3~3 | Y~Y~N~N | Pit ID is not provided~Pit ID is not line with common nomenclature~Pit ID is blocked by CWT assy.~Pit ID is not visible | Y~Y~Y~Y | 1 | 1 | 1~0.333333333~0.333333333~0.333333333 | 1~0.333333333~0.333333333~0.333333333 | 0 | 0 | M | 1 | [value-18] | 4 | 8
2 | LIFT | PIT | PIT CONDITION | 1. Pit should be dry & clean~ 2. Surface should be finished and strong~ 3. No projections, uneven surfaces on pit floor or on walls~ 4. No water seepage~ 5. Pit should not be used as a storage area.~ 6. All cable/ wores should be neatly bunched, routed & secured | 3~3~3~3~3~3~3~3 | Y~Y~Y~Y~Y~Y~Y~Y | Pit is not cleaned~Oil spill in the pit~Water seepage in pit~Scaffolding pipes/rods are projected ~Hanging pit wires/cables is not routed and secured~Damaged/missing seperation screen~Damaged/defective shaft light in pit floor~Unwanted materials is kept in pit | Y~Y~Y~N~Y~Y~Y~Y | 1 | 1 | 0.111~0.111~0.111~0.111~0.111~0.111~0.111~0.111~0.111 | 0.111~0.111~0.111~0.111~0.111~0.111~0.111~0.111~0.111 | 0 | 1 | M | 1 | [value-18] | 8 | 7
3 | LIFT | PIT | PIT LIGHT & CONTROL | 1. Shaft light extended to pit; cannot be considered.~ 2. Separate pit light with control switch accessible from landing, should be provided~ | 3~3~3~3 | N~Y~Y~Y | Dedicated Pit light and control switch is not provided~Pit light is not working ~Pit light switch need to be relocated to near upper stop switch~Damaged pit light/switch | Y~Y~Y~Y | 1 | 1 | 0.2~0.2~0.2~0.2~0.2 | 0.2~0.2~0.2~0.2~0.2 | 0 | 0 | M | 1 | [value-18] | 4 | 1
4 | LIFT | PIT | PIT UPPER STOP SW. OPERATION | All the STOP switches should be working condition | 4 | N | Upper stop switch is not working | Y | 0 | 0 | 0~0~0 | 0~0~0 | 0 | 0 | A | 1 | [value-18] | 1 | 2
5 | LIFT | PIT | PIT LOWER STOP SW. OPERATION | All the STOP switches should be working condition | 4 | N | Lower stop switch is not working | Y | 0 | 0 | 0~0~0 | 0~0~0 | 0 | 0 | A | 1 | [value-18] | 1 | 3
6 | LIFT | PIT | PIT STOP SW. CONDITION | 1) for pits with depth less than or equal to 1,60 m the stop switch shall be: a. within a vertical distance of minimum 0,40 m above the lowest landing floor and a maximum of 2,0 m from the pit floor; b. within a horizontal distance of maximum 0,75 m from the door frame inner edge;~ 2) for pits with depth greater than 1,60 m, two stop switches shall be provided. | 4~3~3~4~3~3 | Y~Y~Y~Y~Y~Y | Upper stop switch is not provided~Upper Stop switch is not accessible from landing~Upper Stop switch is hanging/ damaged~Lower stop switch is not provided~Lower stop switch should be relocated to within 300 mm to 500 mm from pit floor~Lower Stop switch is hanging/ damaged | Y~Y~Y~Y~Y~Y | 1 | 1 | 0.111~0.111~0.111~0.111~0.111~0.111~0.111~0.111~0.111 | 0.111~0.111~0.111~0.111~0.111~0.111~0.111~0.111~0.111 | 0 | 0 | M | 1 | [value-18] | 6 | 0
7 | LIFT | PIT | PIT LADDER/SAFE ACCESS | 1. Clear width of the ladder shall be at least 0,35 m~ 2. Depth of the steps shall not be less than 25 mm~ 3. In the case of vertical ladders the distance between the steps and the wall behind the ladder shall not be less than 0,15 m.~ 4.Steps shall be designed for a load not less than 1500 N | 3~3~3~3~3~3~3 | Y~Y~Y~Y~N~Y~Y | Ladder fixing is not rigid / missing fasteners to be rectified~Ladder height to be extended up to 1350 mm above landing Sill level~Ladder need to be relocated~Pit ladder is missing~Portable pit ladder available in the pit, should be provided with safety switch~Ladder found rusted/ damaged~Ladder to wall clearance is poor. | Y~Y~Y~Y~N~Y~Y | 1 | 1 | 0.143~0.143~0.143~0.143~0.143~0.143~0.143 | 0.143~0.143~0.143~0.143~0.143~0.143~0.143 | 0 | 0 | M | 1 | [value-18] | 7 | 0
8 | LIFT | PIT | BUFFERS & CONDITION | 1. Buffer unit should be vertical~ 2. Rigid fixing~ 3. No Rust~ 4. If Hydraulic, sufficient oil level~ 5. Oil monitoring device should be available~ 6.Electrical switch provided and operational for hydraulic buffer~ 7. Name plate with correct rating and speed details. | 4~3~4~4~4~4~3~3~3~3~3~4~3~3~3~4 | Y~Y~Y~Y~Y~Y~Y~N~Y~Y~Y~Y~N~Y~Y~Y | Missing --- buffer striking plate should be installed on priority~--- buffer is not in line with striking plate~Poor oil level to be rectified in --- buffer~Excess oil level to be rectified in --- buffer~--- buffer is empty and oil to be filled on priority~ --- buffer switch & mechanism is not functional~--- buffer switch is not earthed ~--- buffer switch is missing, recommended~Under rated --- buffer is installed~--- buffer is rusted~--- buffer oil inlet cap is missing ~--- buffer is not vertical(Not in plumb)~--- buffer assembly is shaking~--- buffer mounting bolts are loose /missing~--- buffer oil level montior is missing~PU buffer found damaged | Y~Y~N~Y~Y~Y~N~N~N~Y~N~N~Y~Y~Y~Y | 1 | 1 | 0.063~0.063~0.063~0.063~0.063~0.063~0.063~0.063~0.063~0.063~0.063~0.063~0.063~0.063~0.063~0.063 | 0.063~0.063~0.063~0.063~0.063~0.063~0.063~0.063~0.063~0.063~0.063~0.063~0.063~0.063~0.063~0.063 | 0 | 0 | M | 1 | [value-18] | 16 | 5
9 | LIFT | PIT | CAR RUN BY | 1. Car runby should be from >150 mm to <650 mm. | 3~3 | Y~Y | Car Run by ---mm is inadequate to the minimum of 150 mm~ Car Run By ---mm is excess. | Y~Y | 1 | 1 | 0.5~0.5 | 0.5~0.5 | 0 | 0 | A | 1 | [value-18] | 2 | 0
10 | LIFT | PIT | CWT RUN BY | 1. CWT runby should be from >150 mm to <900 mm.~ 2. When CWT run by is up to 900 mm and is buffered, there should be sufficient gap from car top nearest striking point to overhead ceiling. | 3~5~3 | Y~Y~Y | CWT run by ---mm is inadequate to the minimum of 150 mm~CWT run by is less than 50 mm~CWT run by ---mm is in excess | Y~Y~Y | 1 | 1 | 0.333333333~0.333333333~0.333333333 | 0.333333333~0.333333333~0.333333333 | 0 | 0 | A | 1 | [value-18] | 3 | 6
11 | LIFT | PIT | CAR OIL DRAIN TRAY CONDITION | 1. Oil drain trays should be in correct position.~ 2. No oil spill around the tray or guide rail~ 3. Not applicable for roller guides | 3~3~3~3~0 | Y~Y~Y~Y~N | Car Oil drain trays are missing~Oil Drain trays are not clean~Oil Drain trays are not in position~Oil Drain trays found damaged~Not applicable | Y~Y~Y~Y~N | 1 | 1 | 0.25~0.25~0.25~0.25 | 0.25~0.25~0.25~0.25 | 0 | 0 | M | 0 | [value-18] | 5 | 0
12 | LIFT | PIT | CWT OIL DRAIN TRAY CONDITION | 1. Oil drain trays should be in correct position.~ 2. No oil spill around the tray or guide rail~ 3. Not applicable for roller guides | 3~3~3~3~0 | Y~Y~Y~Y~N | CWT Oil drain trays are missing~Oil Drain trays are not clean~Oil Drain trays are not in position~Oil Drain trays found damaged~Not applicable | Y~Y~Y~Y~N | 1 | 1 | 0.25~0.25~0.25~0.25 | 0.25~0.25~0.25~0.25 | 0 | 0 | M | 0 | [value-18] | 5 | 0
13 | LIFT | PIT | DOWN FINAL LIMIT SWITCH CONDITION /OPERATION | 1. Metal body should be earthed~ 2. Roller should have free movement~ 3. Should contact at center width of the cam body~ 4. Roller pressure should be sufficient- 5. Limit sw. body should have sufficient clearance with the cam | 3~3~3~5~3~4 | Y~N~Y~N~Y~Y | Limits switches are not earthed~Limits switch roller is stuck/not rotating~Limits switch roller is not in centre of the cam width~Down final Limit switch is not working~Limit switch terminal cover is missing~Limit switch roller found damaged | N~N~N~Y~N~Y | 0.5 | 0.5 | 0.0833~0.0833~0.0833~0.0833~0.0833~0.0833 | 0.0833~0.0833~0.0833~0.0833~0.0833~0.0833 | 0 | 0 | M | 1 | [value-18] | 6 | 4
14 | LIFT | PIT | TENSION PULLEY CONDITION | 1. Pulley arm in horizontal plane and or up to 30 degree above is acceptable~ 2. Pulley arm in horizontal plane and or within 30 degree below is acceptable~ 3. Pulley shall be clean and smooth in operation.~ 4. Pulley needs to be guarded~ 5. There shall an electrical monitoring sw. | 3~3~3~4~3 | Y~N~Y~Y~Y | Tension pulley is sagged~Tension pulley is noisy~Tension pulley is not clean~Governor rope is rubbing with pulley guard & noisy~ Pulley guard is not provided | Y~N~Y~Y~Y | 1 | 1 | 0.091~0.091~0.091~0.091~0.091~0.091~0.091~0.091~0.091~0.091~0.091 | 0.091~0.091~0.091~0.091~0.091~0.091~0.091~0.091~0.091~0.091~0.091 | 0 | 0 | A | 1 | [value-18] | 5 | 0
15 | LIFT | PIT | TENSION PULLEY SWITCH CONDITION | 1. Switch should be activated when the pulley is sagged 30 degree and more below the horizontal plane | 2~3~4~3~3 | Y~Y~N~Y~Y | Tension pulley switch is not installed, recommended~Tension pulley switch is not aligned~Tension pulley switch is not functioning~Tension pulley switch is not earthed~Tension pulley switch is cover is damaged/ missing | Y~Y~N~Y~Y | 1 | 1 | 0.091~0.091~0.091~0.091~0.091~0.091~0.091~0.091~0.091~0.091~0.091 | 0.091~0.091~0.091~0.091~0.091~0.091~0.091~0.091~0.091~0.091~0.091 | 0 | 0 | A | 1 | [value-18] | 5 | 0
16 | LIFT | PIT | SCREEN GUARD CONDITION | 1. CWT screen guard bottom should be overlapping the CWT bottom when rested and compressed the buffer piston ~ 2. Screen guard top shall be up to a minimum height of 2.0 m from the pit floor~ 3.the width shall be at least equal to that of the counterweight or balancing weight | 4~3~4~3~3~4 | Y~Y~Y~Y~Y~Y | CWT screen guard is not installed ~CWT screen guard to be lowered to overlap the buffer top~Screen guard is rubbing with CWT~Screen guard is damaged~Screen guard height is less than minimum of 2 meters from pit floor~Screen guard is not covering the width of the CWT | Y~Y~Y~Y~Y~Y | 1 | 1 | 0.2~0.2~0.2~0.2~0.2 | 0.2~0.2~0.2~0.2~0.2 | 0 | 0 | M | 1 | [value-18] | 6 | 0
17 | LIFT | PIT | COMPENSATION CHAIN/ ROPE CONDITION | 1. Comp. chain hitch shall be additionally secured with lacing~ 2. Shall not rub with the floor, screen guard and any other components~ 3. Chain movement shall be smooth and noise less. | 4~4~3~3~4~3~3~3~4~0 | Y~Y~N~Y~Y~Y~Y~N~Y~N | Comp. chain loop is closer/ rubbing with pit floor~Comp. guide is stuck/ damaged~Comp. chain/ rope is noisy~Comp. chain Hitch to be secured with additional lacing at car bottom~Comp. chain / rope found rusted~Comp. chain / rope found damaged~Comp. chain guide roller is damaged.~Comp. rope tension should be equalized~Comp. rope Hitch to be secured with check nut & split pins~Not provided, not applicable | Y~Y~N~Y~Y~Y~Y~N~Y~N | 1 | 1 | 0.0909~0.0909~0.0909~0.0909~0.0909~0.0909~0.0909~0.0909~0.0909~0.0909~0.0909 | 0.0909~0.0909~0.0909~0.0909~0.0909~0.0909~0.0909~0.0909~0.0909~0.0909~0.0909 | 0 | 0 | M | 0 | [value-18] | 10 | 0
18 | LIFT | PIT | TRAVELLING CABLE CONDITION | 1. There shall not be any twist in the cable at least between midway hanger to car bottom hanger~ 2. Cable shall not hit with any component of the pit~ 3. There shall be sufficient gap from pit floor to the cable loop. Ie: When the car is rested on buffer with compressed condition, cable should have atleast 100 to 150 mm gap with pit floor~ 4. There shall be no physical damages in the cable~ 5. Cable should be secured properly with the hanger at car bottom. | 3~3~3~4~4~3~4 | Y~Y~Y~Y~N~Y~Y | Travelling Cable is rubbing with car body~Travelling Cable is rubbing with pit ladder~Cable loop is closer / touching the pit floor~Car bottom hanger is missing/ damaged~Travelling cable found twisted~Excess cable length is not routed & not secured at car bottom~Travelling cable found damaged | Y~Y~Y~Y~N~Y~Y | 1 | 1 | 0.1428~0.1428~0.1428~0.1428~0.1428~0.1428~0.1428 | 0.1428~0.1428~0.1428~0.1428~0.1428~0.1428~0.1428 | 0 | 0 | M | 1 | [value-18] | 7 | 0
19 | LIFT | PIT | CONDITION OF CAR BOTTOM | 1. Car bottom should be clean and no rust.~ 2. Jack bolts should be positioned and locked with check nuts~ 3. Upthrust bolts/ mechanism should be intact~ 4. Car bottom sheaves and ropes should be guarded suitably~ 5. Car bottom light should be provided and guarded | 3~3~3~3~3~3~3~4~2 | Y~Y~Y~Y~Y~Y~Y~Y~N | Car bottom is not clean~ Car bottom is rusted~Jack bolts are missing~Jack bolt gap is poor/ hitting~ Missing check nuts in jack bolts~Wiring is not routed and not secured~Brace rod (Diagonal rod) bolts / check nuts are loose.~Car bottom light is not guarded~Car bottom bulb is missing/ not working. | Y~Y~Y~Y~Y~Y~Y~Y~N | 1 | 1 | 0.05~0.05~0.05~0.05~0.05~0.05~0.05~0.05~0.05~0.05 | 0.05~0.05~0.05~0.05~0.05~0.05~0.05~0.05~0.05~0.05 | 0 | 0 | M | 1 | [value-18] | 9 | 0
20 | LIFT | PIT | OVERLOAD DEVICE | 1. Overload device (if provided) should be in correct position and wired neatly~ 2. Car bottom cables should be routed and secured properly~ | 4~4~4~4 | N~Y~Y~Y | Not provided~Overload device is missing~Overload device found damaged ~Overload device mounting is improper/not working | N~Y~Y~Y | 1 | 1 | 0.05~0.05~0.05~0.05~0.05~0.05~0.05~0.05~0.05~0.05 | 0.05~0.05~0.05~0.05~0.05~0.05~0.05~0.05~0.05~0.05 | 0 | 0 | A | 1 | [value-18] | 4 | 0
21 | LIFT | PIT | CONDITION OF SAFETY GEAR | 1. Safety gear should be aligned properly with equal gaps with guide rail~ 2. Assembly and mechanism should be clean and lubricated with free movement~ 3. All the Safety wedges should be contacting the guide rails at the same time when tested | 3~3~4 | Y~N~N | Safety gear assembly is not clean~Safety gear gap is uneven~Safety gear is rubbing with guide rails | Y~N~N | 1 | 1 | 0.2~0.2~0.2~0.2~0.2 | 0.2~0.2~0.2~0.2~0.2 | 0 | 0 | M | 1 | [value-18] | 3 | 0
22 | LIFT | PIT | CONDITION OF SLIDING GUIDE SHOE/ GUIDE ROLLERS | 1. Guide shoes should be clean and no excess gap/ play with the guide rails~ 2. Guide shoe liner thickness should be sufficient and not worn out 3. If the guide shoes are spring loaded, spring tension should be as per standard recommendations | 3~3~3~4~3~4~3~4 | Y~N~N~N~N~Y~N~Y | Guide shoes are not clean~Guide shoe liners are wornout~Guide shoe play is more~ Guide shoe liner/s are missing/ damaged~ Roller guides tension is uneven/excess play~ Roller guide tyre found damaged~Roller guides are noisy~Roller guides tension spring found damaged | Y~N~N~N~N~Y~N~Y | 1 | 1 | 0.2~0.2~0.2~0.2~0.2 | 0.2~0.2~0.2~0.2~0.2 | 0 | 0 | M | 1 | [value-18] | 8 | 0
23 | LIFT | PIT | CWT SAFETY GEAR | 1. If accessible spaces do exist below the well, the base of the pit shall be designed for an imposed load of at least 5 000 N/m2~ 2. And the counterweight shall be equipped with safety gear.~ 3. In addition, it is recommended to provide double slab for the lift pit.~ NOTE: 1 Lift wells should preferably not be situated above a space accessible to persons.~ 2 Enclosing projected area of the lift shaft under the pit inaccessible spaces will not nullify above provisions. | 0~5~4 | N~Y~Y | Not applicable~ CWT safety gear is not provided,access below the pit floor should blocked permanently~CWT safety gear is provided,access below the pit floor should blocked permanently | N~Y~Y | 1 | 1 | 0.05~0.05~0.05~0.05~0.05~0.05~0.05~0.05~0.05~0.05 | 0.05~0.05~0.05~0.05~0.05~0.05~0.05~0.05~0.05~0.05 | 0 | 0 | M | 0 | [value-18] | 3 | 0
24 | LIFT | CABIN | CABIN IDENTIFICATION | 1. When there are more than one lift in a building, Proper ID is mandatory~ 2. ID should be inline with common nomenclature~ 3. Display of ID should be permanent | 4~3~3 | Y~Y~Y | Cabin ID is missing~Cabin ID not in line with common nomenclature~Cabin ID is not visible | Y~Y~Y | 1 | 1 | 0.333~0.333~0.333 | 0.333~0.333~0.333 | 0 | 0 | M | 1 | [value-18] | 3 | 25
25 | LIFT | CABIN | CAPACITY PLATE | 1. Providing capacity plate is mandatory~ 2. Capacity with the details of No. of passenger & Kilogram should be clearly visible~ 3. Capacity plate & details should be permanently available | 3~3~3~3 | N~Y~Y~N | Capacity plate is missing~Capacity plate is faded~Capacity is mismatching~Capacity plate is not visible | N~Y~Y~N | 1 | 1 | 0.25~0.25~0.25~0.25 | 0.25~0.25~0.25~0.25 | 0 | 0 | M | 1 | [value-18] | 4 | 0
26 | LIFT | CABIN | CABIN SAFETY INSTRUCTIONS | 1. Providing safety instructions is mandatory~ 2. Do's & Donts should be clearly mentioned.~ 3. Emergency contact details & guidance should be provided~ 4. Safety instructions should be permanently available. | 3~3~3~3 | N~Y~N~N | Instruction plate is missing~Instructions are faded~Instruction plate is not visible~No smoking sign/instruction is missing. | N~Y~N~N | 1 | 1 | 0.25~0.25~0.25~0.25 | 0.25~0.25~0.25~0.25 | 0 | 0 | M | 1 | [value-18] | 4 | 0
27 | LIFT | CABIN | CAR LIGHTING | 1. All lights should be in working condition and no fused lights~ 2. Light intensity of at least 100 lux on the control devices and at 1 m above the floor at any point not less than 100 mm from any wall. | 3~3~4 | Y~N~Y | Some cabin lights are fused~Cabin light illumination is poor~Cabin lights are not working | Y~N~Y | 1 | 1 | 0.25~0.25~0.25~0.25 | 0.25~0.25~0.25~0.25 | 0 | 0 | M | 1 | [value-18] | 3 | 0
28 | LIFT | CABIN | FALSE CEILING CONDITION | 1. All lights should be in working condition and no fused lights~ 2. False ceiling should clean and no damages or missing portions. | 3~3~3 | Y~Y~Y | False ceiling is missing ~ False ceiling is damaged~False ceiling is not clean | Y~Y~Y | 0 | 0 | 0~0 | 0~0 | 0 | 0 | M | 1 | [value-18] | 3 | 0
29 | LIFT | CABIN | PROVISION OF EMERGENCY LIGHT | 1. E. Light is mandatory~ 2. E. Light luminus should be to a miminum of 20 LUX~ 3. E. light duration should be available for minimum of 1 hour~ 5. Alarm & I.Com buttons should be visible to the user in E.light~ 6. Alarm symbol should be clearly visible E. light | 3~3~3 | N~Y~N | Emergency light is working for shorter duration~Emergency light brightness is poor~Missing Emergency light should be installed | N~Y~N | 2 | 2 | 2~0~0.5~0.5~0.5 | 0~0~0.5~0.5~0.5 | 0 | 0 | M | 1 | [value-18] | 3 | 0
30 | LIFT | CABIN | FUNCTIONING OF EMERGENCY LIGHT | 1. E. Light is mandatory~ 2. If the cabin lights are working through UPS and working when the during the power failure is acceptable | 4~4 | Y~N | Not working~Not provided | Y~Y | 0 | 0 | 0~0 | 0~0 | 1 | 0 | A | 1 | [value-18] | 2 | 18
31 | LIFT | CABIN | FUNCTIONING OF EMERGENCY ALARM | 1. Alarm is mandatory~ 2. Confirmation of Alarm function to be provided to the passenger~ 4. Alarm button should be yellow in colour & visible even in darkness. | 4~4 | N~N | Not working~Not provided | Y~Y | 0 | 0 | 0~0 | 0~0 | 1 | 0 | A | 1 | [value-18] | 2 | 17
32 | LIFT | CABIN | PROVISION OF EMERGENCY ALARM | 1. It should be audible to the main lobby/ security even when the car is at top floor~~ 2. Confirmation of Alarm function to be provided to the passenger~ 3. Alarm button should be yellow in colour & visible even in darkness. | 3~4~4 | N~Y~N | Audibility is poor~Alarm unit is fixed in cartop, not audible in main lobby floor~Alarm unit is missing | N~Y~N | 0 | 0 | 0~0~0 | 0~0~0 | 0 | 0 | A | 1 | [value-18] | 3 | 0
33 | LIFT | CABIN | FUNCTIONING OF INTERCOM OPERATION | 1. It is Mandatory requirement for the building above 15 M high~ 2. It should be 3 ways system~ 3. I.Com button should be clearly visible to the user | 4~4 | N~N | Not working~Not provided | Y~Y | 2 | 2 | 2~1~0.5~0.5~0.5~0.5 | 0~1~0.5~0.5~0.5~0.5 | 1 | 0 | M | 1 | [value-18] | 2 | 19
34 | LIFT | CABIN | PROVISION OF INTERCOM FUNCTION | 1. Mandatory requirement~ 2. Machine room, Security and or BMS should be in communication from cabin~ 3. I.Com button should be clearly visible to the user~ | 3~3~3~3 | N~N~Y~N | 3rd hand set is not provided at BMS or Security room~Intercom is noisy~Intercom unit found damaged~Intercom audio is feeble. | N~N~Y~N | 0 | 0 | 0~0~0~0~0 | 0~0~0~0~0 | 0 | 0 | M | 1 | [value-18] | 4 | 0
35 | LIFT | CABIN | FUNCTION OF ARD | 1. It is not mandatory, when DG set with AMF panel is available | 4~4 | N~N | Not working~Not provided | Y~Y | 2 | 2 | 3~0~3~0.6~0.6~0.6~0.6 | 0~0~0~0.6~0.6~0.6~0.6 | 1 | 0 | M | 1 | [value-18] | 2 | 16
36 | LIFT | CABIN | PROVISION OF ARD | 1. During ARD, E. light & 1 no. fan should be functional~ 2. ARD should be able take the lift to the highest rise of the floor 3. At floor level, doors should be opened fully & remain for 15 Seconds | 4~3~3~3~3~4 | N~N~N~N~N~Y | Doors are not opening at the end of ARD operation~ARD Mode door time (Dwell time) is poor~ARD audio is not working,recommended~ARD visual indicator is not working,recommended~ARD audio & visual indicator is not working, recommended~Level difference is exceeding the maximum limit of 40 mm. | N~N~N~N~N~Y | 0 | 0 | 0~0~0~0~0 | 0~0~0~0~0 | 0 | 0 | M | 1 | [value-18] | 6 | 0
37 | LIFT | CABIN | CAR DOOR CONDITION | 1. In closed condition, gap from door panel to side jamb, transom panel and to the sill shall not exceeed 6 mm~ 2. No scratches or dent on the panels.~ 3. In closed condition, door edges should be seated to gether evenly and without any gap~ 4. In open condition, door edges should be inline with jamb post evenly | 4~3~3~3~3~3 | Y~Y~Y~Y~Y~Y | Door to jamb gap is exceeding 6 mm.~Door to jamb gap is less than 3 mm.~ Uneven jamb gap ~Car door/bumper is rubbing with the Sill~ Door dent /Scratches found~ Door panel found bend | Y~Y~Y~Y~Y~Y | 1 | 1 | 0.143~0.143~0.143~0.143~0.143~0.143~0.143 | 0.143~0.143~0.143~0.143~0.143~0.143~0.143 | 0 | 0 | A | 1 | [value-18] | 6 | 0
38 | LIFT | CABIN | CAR DOOR OPERATION | 1. Door operation should be smooth & no friction~ 2. Doors should open fully~ 3. Final opening & closing should not be banging/ hitting | 3~3~3~3 | N~N~N~N | Door operation is noisy~Doors are banging~Doors are not closing fully~Doors are not opening fully | Y~N~N~N | 1 | 1 | 0.25~0.25~0.25~0.25 | 0.25~0.25~0.25~0.25 | 0 | 0 | A | 1 | [value-18] | 4 | 24
39 | LIFT | CABIN | CAR DOOR SAFETY SENSOR/ MECHANISM | 1. The protective device (for example, light curtain) shall cover the opening over the distance between at least 25 mm and 1600 mm above the car door sill~ 2. Fixing should be rigid~ 3. No physical damages | 3~3~4~3~3 | N~N~N~Y~Y | Door Sensor fixing is not rigid~Door sensor is malfunctioning~Door sensors are not working.~Door sensor found damaged~Door sensor is installed above 25 mm from sill level. | N~Y~Y~Y~N | 1 | 1 | 0.2~0.2~0.2~0.2~0.2 | 0.2~0.2~0.2~0.2~0.2 | 0 | 0 | A | 1 | [value-18] | 5 | 15
40 | LIFT | CABIN | LEVELLING | 1. Level difference shall be with 5 mm | 3 | Y | Level difference is exceeding the maximum limit of 5 mm | Y | 1 | 1 | 0.25~0.25~0.25~0.25 | 0.25~0.25~0.25~0.25 | 0 | 0 | A | 1 | [value-18] | 1 | 22
41 | LIFT | CABIN | CAR SILL TO LANDING SILL GAP | 1. Sill gap should not be more than + 2 mm of 30 mm or as per GAD~ 2. Gap between car Sill to Landing Sill should be even | 3~3~3 | Y~Y~Y | Uneven gaps on both ends~ Sill gap --- mm is exceeding -- mm~Sill gap --- mm is poor and less than -- mm | Y~Y~Y | 0 | 0 | 0~0 | 0~0 | 0 | 0 | A | 1 | [value-18] | 3 | 0
42 | LIFT | CABIN | START, ROLL BACK & STOP JERKS | 1. Starting & stopping should be smooth without any kind of jerk impact to the passenger | 3~3~3 | N~N~N | Starting rollback (jerk)~Starting jerk~Stopping jerk | N~N~N | 1 | 1 | 0.333~0.333~0.333 | 0.333~0.333~0.333 | 0 | 0 | A | 1 | [value-18] | 3 | 0
43 | LIFT | CABIN | RIDING PERFORMANCE | 1. There shall not be any sway/ play in the cabin~ 2. No jerk impact on X-Y- Z axis during the travel~ 3. No knocks, hitting, rubbing or any kind of vibration in the cabin. | 3~3~3~3~3~3 | N~N~N~N~N~N | Cabin sway /play is is observed~Cabin vibration is observed~Cabin creak noise is observed~Cabin knocks are observed~X-Y jerks in riding is observed~ Cabin Riding is noisy | N~Y~N~Y~N~Y | 1 | 1 | 0.167~0.167~0.167~0.167~0.167~0.167 | 0.167~0.167~0.167~0.167~0.167~0.167 | 0 | 0 | A | 1 | [value-18] | 6 | 23
44 | LIFT | CABIN | CABIN INTERIOR CONDITION | 1. Cabin interior should be intact & clean.~ 2. Panels are fixed rigidly with each other & surface should be even.~ 3. Kick plates should be in position and rigidly fixed | 3~3~3~3~3~3 | Y~Y~Y~Y~Y~Y | Cabin kick plates found loose~Protective covers are not removed~Cabin kick plates are missing~Cabin mirror is damaged~Cabin panels are covered with plywood - Ventilation is blocked~Cabin panel joints gaps/ uneven surface. | Y~Y~Y~Y~Y~Y | 1 | 1 | 0.143~0.143~0.143~0.143~0.143~0.143~0.143 | 0.143~0.143~0.143~0.143~0.143~0.143~0.143 | 0 | 0 | M | 1 | [value-18] | 6 | 0
45 | LIFT | CABIN | CABIN DISPLAY CONDITION | 1. Display should be bright and readable~ 2. Floor designations in buttons & display should be inline with each other~ 3. If date & time is provided, it should be inline with local time zone. | 4~3~3~3 | Y~Y~Y~Y | Cabin display is not working~Multimedia display is not working~Display Date/ Time is mismatching~Cabin display is malfunctioning | Y~N~N~Y | 1 | 1 | 0.167~0.167~0.167~0.167~0.167~0.167 | 0.167~0.167~0.167~0.167~0.167~0.167 | 0 | 0 | M | 1 | [value-18] | 4 | 10
46 | LIFT | CABIN | C.O.P CONDITION | 1. All buttons should be in good physcial & operating condition~ 2. Button names should be clearly visible and readable~ 3. (If applicable) Braille marking should be available & intact for all buttons~ 4. The above requirements are applicable for Aux. C.O.P also. | 3~3~3~3~3 | Y~N~N~N~N | C.O.P service panel door is damaged/ missing~ C.O.P is not seated~ C.O.P fixing is loose~Aux C.O.P is not seated~Aux C.O.P fixing is loose | Y~N~N~N~N | 1 | 1 | 0.111~0.111~0.111~0.111~0.111~0.111~0.111~0.111~0.111 | 0.111~0.111~0.111~0.111~0.111~0.111~0.111~0.111~0.111 | 0 | 0 | M | 1 | [value-18] | 5 | 0
47 | LIFT | CABIN | C.O.P OPERATIONS | 1. All buttons/ switches should be in good operating condition~ 2. Buttons light should be sufficiently bright & visible~ 2.This is applicable for Aux. C.O.P also | 3~3~3~3~3~3~3 | Y~Y~Y~N~Y~Y~N | C.O.P button--- is/are faded ~C.O.P button--- is/are damaged~Missing Braille markings in button/s~ C.O.P button --- illumination is poor/ not working~Aux C.O.P button--- is/are faded ~Aux C.O.P button--- is/are damaged~ Aux C.O.P button --- illumination is poor/ not working | N~Y~N~Y~N~Y~Y | 1 | 1 | 0.143~0.143~0.143~0.143~0.143~0.143~0.143 | 0.143~0.143~0.143~0.143~0.143~0.143~0.143 | 0 | 0 | M | 1 | [value-18] | 7 | 9
48 | LIFT | CABIN | FLOORING CONDITION | 1. There shall not be any gap between tiles or panles~ 2. Finished surface of the flooring should be inline with Car Sill.~ 3. No damages or uneven surface should be there on the flooring | 3~3~3~3 | Y~Y~Y~Y | Flooring marble / tiles found damaged/ cracked~Gap in flooring marble/tiles~Cabin flooring is not in line with Sill level~Cabin flooring is not done | Y~Y~Y~Y | 1 | 1 | 0.333~0.333~0.333 | 0.333~0.333~0.333 | 0 | 0 | M | 1 | [value-18] | 4 | 0
49 | LIFT | CABIN | FAN WORKING CONDITON | 1. All fan should be in working condition~ 2. Fans ooperation should be somooth and no abnormal noise~ 3. Air circulation should be sufficient | 3~3~3~3~3~3 | N~Y~N~N~N~N | Fan operation is noisy~Cabin fan --- no/s is missing~Fan switch is not working~Fan auto OFF function is not working~Cabin fan is not working~ Cabin fan ---no/s not working | N~Y~N~N~N~N | 1 | 1 | 0.25~0.25~0.25~0.25 | 0.25~0.25~0.25~0.25 | 0 | 0 | M | 1 | [value-18] | 6 | 0
50 | LIFT | CABIN | HAND RAILS CONDITION | 1. Hand rail fixing should be rigid~ 2. Handrail should be at a height between 0.90 m and 1.10 m. ~ 3. This handrail shall be fastened independently from the glass. | 3~3~3~2 | N~Y~Y~N | Hand rail fixings are not rigid~Hand rail is missing~Unused Handrail fixing holes found~Hand rail is not provided-recommended | N~Y~Y~N | 1 | 1 | 0.333~0.333~0.333 | 0.333~0.333~0.333 | 0 | 0 | M | 0 | [value-18] | 4 | 0
51 | LIFT | CABIN | CABIN VENTILATION | 1. Ventilation apertures to be in the upper and lower parts of the car.~ 2. The gaps round the car doors may be taken into account of the area of ventilation holes, up to 50 percent of the required effective area~ 3. Ventilation apertures shall be built or arranged in such a way that it is not possible to pass a straight rigid rod 10 mm in diameter through the car walls from the inside. | 4~4~3~3 | Y~N~N~Y | Cabin ventilation is blocked by cabin interiors~Cabin ventilation is not provided~Cabin ventilation is poor~Excess size holes should be protected from intrusion. | Y~N~N~Y | 1 | 1 | 0.25~0.25~0.25~0.25 | 0.25~0.25~0.25~0.25 | 0 | 0 | M | 1 | [value-18] | 4 | 0
52 | Lift | CABIN | TOE GUARD | 1. Toe guard width should be at least to the full width of the clear landing entrance, which it faces~ 2. The height of the vertical portion shall be at least 0.75 m~ 3. This vertical section shall be extended downwards by a chamfer whose angle with the horizontal plane shall be at least 60°. | 5~4~3~3~3 | Y~Y~N~Y ~Y | Toe guard is missing ~Toe Guard height ---mm, is less than the minimum of 750mm~Toe guard fixing is not rigid ~ Toe guard is rusted~Missing screws/ bracket in Toeguard fixing. | Y~N~N~N ~N | 1 | 1 | 0.25~0.25~0.25~0.25 | 0.25~0.25~0.25~0.25 | 0 | 0 | M | 1 | [value-18] | 5 | 26
53 | LIFT | CABIN | LIFT LICENSE DISPLAY IN ELEVATOR CABIN | 1. When applicable, license copy should be displayed in the cabin | 2~3~0 | N~Y~N | License available and not displayed in cabin~Displayed license has expired~License is not applicable in this region. | N~Y~N | 0 | 0 | 0~0~0~0 | 0~0~0~0 | 0 | 0 | M | 0 | [value-18] | 3 | 0
54 | LIFT | CAR TOP | MAINTENANCE / INSPECTION SWITCHES | 1. Inspection sw. shall be bi-stable, shall be protected against involuntary operation & clealry indicated~ 2. Push buttons should be clearly indicated & protected against accidental operation~ 3. Easily accessible position and no more than 1 m from the entry point for inspection or maintenance personnel.~ 4. No physical damages | 4~4~4~3~3 | N~N~N~Y~Y | Up direction switch/ button is not working~Down direction switch/ button is not working~INSPECTION/NORMAL switch is not working~INSPECTION/NORMAL switch found damaged~Direction button/s found damaged | Y~Y~Y~N~N | 0.5 | 0.5 | 0.071~0.071~0.071~0.071~0.071~0.071~0.071 | 0.071~0.071~0.071~0.071~0.071~0.071~0.071 | 0 | 0 | M | 1 | [value-18] | 5 | 27
55 | LIFT | CAR TOP | FUNCTION OF STOP SWITCH | Inspection sw. shall be bi-stable, shall be pro... | 4~3 | N~Y | STOP button is not functional~STOP button found damaged | Y~N | 1 | 1 | 0.05~0.05~0.05~0.05~0.05~0.05~0.05~0.05~0.05~0.05 | 0.05~0.05~0.05~0.05~0.05~0.05~0.05~0.05~0.05~0.05 | 0 | 0 | M | 1 | [value-18] | 2 | 30
56 | LIFT | CAR TOP | DEDICATED GUARDED HAND LAMP | Dedicated guarded lamp should be provided in each car top | 3~3~3 | Y~Y~N | Guarded hand lamp is missing~Car top hand lamp is not guarded~Car top lamp is not working. | Y~N~Y | 0.5 | 0.5 | 0.167~0.167~0.167 | 0.167~0.167~0.167 | 0 | 0 | M | 1 | [value-18] | 3 | 29
57 | LIFT | CAR TOP | IDENTIFICATION OF CAR TOP | 1. When there is more than one elevator in a building, identification is is mandatory~ 2. Indetification should be inline with common nomenclature | 3~3~3 | Y~Y~N | Identification should be rectified as per common nomenclature~Car top identification is missing~Car top identification is not visible | Y~Y~N | 0.5 | 0.5 | 0.1666~0.1666~0.1666 | 0.1666~0.1666~0.1666 | 0 | 0 | M | 1 | [value-18] | 3 | 35
58 | LIFT | CAR TOP | CONDITION OF CAR TOP | 1.Car roof shall resist a minimum force of 2000 N at any position on an area of 0.30 m X 0.30 m without permanent deformation~ 2. All components should be intact, wiring to be routed and secured 3. Car top should not be used as storage. | 3~3~4~3 | Y~Y~N~Y | Car top is not clean~Unwanted materials found on car top~Car top is bending when stepped on & not strong~Car top is rusted | Y~N~Y~Y | 0.5 | 0.5 | 0.0833~0.0833~0.0833~0.0833~0.0833~0.0833 | 0.0833~0.0833~0.0833~0.0833~0.0833~0.0833 | 0 | 0 | M | 1 | [value-18] | 4 | 34
59 | LIFT | CAR TOP | 3 PIN SOCKET | 3 Pin socket should be provided with independent switch control | 3~3 | Y~N | Found damaged~Switch control is not available | Y~N | 0.5 | 0.5 | 0.167~0.167~0.167 | 0.167~0.167~0.167 | 0 | 0 | M | 1 | [value-18] | 2 | 0
60 | LIFT | CAR TOP | BALUSTRADE OF CAR TOP | 1. Where the free distance in a horizontal plane, beyond and perpendicular to the outer edge of the car roof to the wall exceeds 0.30 m, a balustrade shall be provided~ 2. Car roof shall be provided with a toe board > 0.10 m high~ 3. Balustarde shall consist of a handrail and an intermediate bar at half the height~ 4. Balustrade height should be; a) 700 mm where the distance is up to 500 mm b) 1100 mm where the distance exceeds 500 mm | 3~3~3~3~3~4~4 | N~Y~Y~Y~N~N~N | Balustrade height is less than the 700 mm~Balustrade mid bar is missing~Balustrade found Damaged/ bend~Balustrade is provided only on rear~Balustrade is shaking~Balustrade is not installed & Horizontal distance ---mm is exceeding 300 mm~Horizontal distance ---mm is exceeding 500 mm, balustrade height should be extended to 1100 mm | N~Y~Y~Y~N~N~N | 0.5 | 0.5 | 0.062~0.062~0.062~0.062~0.062~0.062~0.062~0.062 | 0.062~0.062~0.062~0.062~0.062~0.062~0.062~0.062 | 0 | 0 | M | 1 | [value-18] | 7 | 0
61 | LIFT | CAR TOP | GUARDED SMOKE VENT | 1. The well shall have permanent vent immediately under the M/C room not less than 2M² / lift with wire mesh that rejects the ball size of 25mm dia | 3~3~3~2 | Y~Y~Y~N | Smoke vent is not guarded~Air duct is not guarded~Smoke vent guard found damaged/ partly removed~Smoke vent is not provided- Information | Y~Y~Y~N | 0.5 | 0.5 | 0.125~0.125~0.125~0.125 | 0.125~0.125~0.125~0.125 | 0 | 0 | M | 0 | [value-18] | 4 | 0
62 | LIFT | CAR TOP | EARTHING OF CAR TOP BODY & ALL ACCESSORIES | Metal parts/ body of lift car and electrical switches, boxes shall be earthed | 3~3 | N~N | Accessories are not earthed~Car top metal body is not earthed | N~N | 0.5 | 0.5 | 0.1666~0.1666~0.1666 | 0.1666~0.1666~0.1666 | 0 | 0 | M | 1 | [value-18] | 2 | 0
63 | LIFT | CAR TOP | EMERGENCY EXIT CONDITION | Condition of Emergency Exit on car top (If provided). Shall have minimum clear opening dimensions of 0,40 m x 0,50 m. And 0,50 m x 0,70 m is preferable. There shall be an electrical sw. confirming the closed position. | 4~3~3~4~0 | Y~Y~Y~N~N | Emergency Exit switch is missing~Emergency Exit door is not closed properly.~Emergency Exit is not accessible, and blocked by false ceiling~Emergency Exit door switch found by-passed~ Not provided, Not applicable | Y~Y~Y~N~N | 0.5 | 0.5 | 0.125~0.125~0.125~0.125 | 0.125~0.125~0.125~0.125 | 0 | 0 | M | 0 | [value-18] | 5 | 0
64 | LIFT | CAR TOP | CONDITION OF TRAVELLING CABLE | 1. Trailing cable shall be in good condition, insulation shall not get frayed or damaged physically. ~ 2. There shall not be any twist in the cable~ 3. Properly supported at top floot & in Midway~ 4. Trailing cable should be routed and secured on car top | 3~3~4~4~4~4 | Y~Y~Y~Y~Y~N | Travelling cable retainer clamp is missing on car top~Travelling cable is not routed and not secured on car top~Travelling cable found damaged at ___ floor~Mid way hanger is damaged~Top hanger is damaged~Travelling cable found twisted. | Y~Y~Y~Y~Y~N | 0.5 | 0.5 | 0.0833~0.0833~0.0833~0.0833~0.0833~0.0833 | 0.0833~0.0833~0.0833~0.0833~0.0833~0.0833 | 0 | 0 | M | 1 | [value-18] | 6 | 0
65 | LIFT | CAR TOP | UP FINAL LIMIT SWITCH CONDITION /OPERATION | 1. Metal body should be earthed~ 2. Roller should have free movement~ 3. Should contact at center width of the cam body~ 4. Roller pressure should be sufficient- 5. Limit sw. body should have sufficient clearance with the cam | 3~3~3~5~3~4 | Y~N~Y~N~Y~Y | Limits switches are not earthed~Limits switch roller is stuck/not rotating~Limits switch roller is not in centre of the cam width~Up final Limit switch is not working~Limit switch terminal cover is missing~Limit switch roller found damaged | N~N~N~Y~N~Y | 0.5 | 0.5 | 0.0833~0.0833~0.0833~0.0833~0.0833~0.0833 | 0.0833~0.0833~0.0833~0.0833~0.0833~0.0833 | 0 | 0 | M | 1 | [value-18] | 6 | 28
66 | LIFT | CAR TOP | INDUCTOR SW. & CAM ALIGNMENT/CONDITION | 1. Floor cam shall have sufficient engagement with the proximity switch~ 2. Gap at all the three sides of the cam with proximity sw. should be equal~ 3. Floor cam should be vertical and no inclinations | 3~3~4 | Y~Y~Y | Floor cam is not in centre with inductor switch~Insufficient engagement of floor cam with inductor switch~Poor running clearance of floor cam with inductor switch | Y~Y~Y | 0.5 | 0.5 | 0.1~0.1~0.1~0.1~0.1 | 0.1~0.1~0.1~0.1~0.1 | 0 | 0 | A | 1 | [value-18] | 3 | 0
67 | LIFT | CAR TOP | SHAFT LIGHTING | 1. Lighting elements shall be protected against mechanical damage.~ 2.At least 50 lux, 1.0 m above the car roof within its vertical projection~ 3. Hoist way lighting shall be provided and in working in order. | 3~3~3~3~3~3 | Y~Y~Y~Y~Y~Y | Shaft lights are not working~Damaged lights/ bulk heads found in the hoist way ~Some of the lights found not working~Light is not working at MRL Machine~Light is not provided at MRL Machine~Shaft lights are not installed | Y~Y~Y~Y~Y~Y | 0.5 | 0.5 | 0.125~0.125~0.125~0.125 | 0.125~0.125~0.125~0.125 | 0 | 0 | M | 1 | [value-18] | 6 | 0
68 | LIFT | CAR TOP | CONDITION OF CWT | 1. CWT top sheave shall be adequately guarded from accidental contact. and from falling objects~ 2. Counterweight stacks are firmly secured to the frame by tie-rod or other suitable means~ 3. CWT should be clean and painted~ 4. Comp. chain hitch should be secured additionally with lacing | 3~4~3~3~4~3~3~3~3 | N~Y~N~Y~N~Y~Y~Y~Y | CWT stack is shaking.~CWT stack is not locked~CWT stack lock found loose / is not secured properly~CWT stack found rusted~CWT sheave is noisy~CWT sheave is not clean~Comp. Chain hitch is not secured with additional lacing at CWT bottom~CWT sheave is not guarded~ Split pin is missing/ not secured at Comp. chain / Comp. rope hitch | N~Y~N~Y~N~Y~Y~Y~Y | 0.5 | 0.5 | 0.0625~0.0625~0.0625~0.0625~0.0625~0.0625~0.0625~0.0625 | 0.0625~0.0625~0.0625~0.0625~0.0625~0.0625~0.0625~0.0625 | 0 | 0 | M | 1 | [value-18] | 9 | 0
69 | LIFT | CAR TOP | CAR TOP WIRING PIPES SADDLING | All wires /Cables should be routed and secured properly | 3~3~3 | Y~Y~Y | Trough cover is missing~ Trough cover screws are missing ~Car top wires/ cables are not secured/not routed | Y~Y~Y | 0.5 | 0.5 | 0.166~0.166~0.166 | 0.166~0.166~0.166 | 0 | 0 | M | 1 | [value-18] | 3 | 0
70 | LIFT | CAR TOP | CONDITION OF LANDING LOCKS, SWITCHES | 1. The lift shall not start if the lever is pressed or the when the lock contact is open~ 2. The lift shall not start if the secondary door contact is open.~ 3.The contact may be provided on only one panel (rapid panel in case of telescopic doors) if the interconnecting mechanism of door panels is so arranged. | 4~4~3~5~4 | N~N~Y~Y~N | Lock play is more~Lock play is poor~Missing lock cover~Landing door contact found by passed at----floor~Lock is not earthed | N~N~N~Y~N | 0.5 | 0.5 | 0.055~0.055~0.055~0.055~0.055~0.055~0.055~0.055~0.055 | 0.055~0.055~0.055~0.055~0.055~0.055~0.055~0.055~0.055 | 0 | 0 | A | 1 | [value-18] | 5 | 33
71 | LIFT | CAR TOP | ALIGNMENT OF DOOR COUPLER | 1. Door coupler to landing Sill clearance should be 10 mm + 2 mm at all floors~ 2. Gaps / running clearance with lock rollers should be equal | 3~3~3~4~4~4 | Y~Y~Y~Y~Y~Y | Unequal coupler gap with lock rollers~Poor engagement of coupler with lock rollers~Coupler gap with landing Sill is poor at ---floor~Coupler is hitting with lock rollers at ---floor~Coupler is hitting with landing sill at ---floor~Coupler is hitting with landing header at ---floor | Y~Y~Y~Y~Y~Y | 0.5 | 0.5 | 0.0714~0.0714~0.0714~0.0714~0.0714~0.0714~0.0714 | 0.0714~0.0714~0.0714~0.0714~0.0714~0.0714~0.0714 | 0 | 0 | A | 1 | [value-18] | 6 | 0
72 | LIFT | CAR TOP | ALIGNMENT OF LOCK & ROLLERS | 1.Landing lock rollers to Car Sill clearance should be 10 mm + 2 mm at all floors.~ 2. Gaps / running clearance with door coupler should be equal | 3~3~3~3 | Y~Y~Y~N | Gap with landing Sill is ---mm ~Engagement with door coupler is --- mm~Lock rollers found damaged at --- floors~Lock rollers are not rotating at --- floors | Y~Y~Y~N | 0.5 | 0.5 | 0.125~0.125~0.125~0.125 | 0.125~0.125~0.125~0.125 | 0 | 0 | A | 1 | [value-18] | 4 | 0
73 | LIFT | CAR TOP | DOOR ROLLERS/SHOE CONDITION | 1. Hanger & upthrust rollers shall have free movement & noiseless~ 2. Upthrust rollers shall have least clearance with the track bottom~ 3. There shall be no rust , damages in the rollers | 3~4~3~3~4~4~4~3~3 | N~Y~N~N~Y~Y~N~N~Y | Door shoes are worn out at ---floor~Missing door shoe to be provided at --- floor~Door rollers mechanical friction at ---floor~Upthrust (Excentric) roller's mechanical friction~Door roller found damaged at ---floor~Damaged upthrust / excentric roller at ---floor~Missing upthrust/ excentric roller at ---floor~Eccentric / upthrust roller gap is more~Rusted aircord rope at ---floor | N~Y~N~N~Y~Y~N~N~Y | 0.5 | 0.5 | 0.055~0.055~0.055~0.055~0.055~0.055~0.055~0.055~0.055 | 0.055~0.055~0.055~0.055~0.055~0.055~0.055~0.055~0.055 | 0 | 0 | A | 1 | [value-18] | 9 | 0
74 | LIFT | CAR TOP | (SOS) SAFETY GEAR SWITCH OPERATION | 1. When the car safety gear is engaged, an electric safety device mounted on the car shall initiate the stopping of the machine before or at the moment of safety gear operation | 3~3~3~5~3~3~5 | Y~Y~Y~N~Y~N~N | Excess switch gap & not aligned~Switch gap is poor~Switch cover is missing/ damaged~SOS is not working ~SOS switch wiring is not routed and not secured~SOS switch is not earthed~SOS is not provided | N~N~N~Y~N~N~Y | 0.5 | 0.5 | 0.083~0.083~0.083~0.083~0.083~0.083 | 0.083~0.083~0.083~0.083~0.083~0.083 | 0 | 0 | M | 1 | [value-18] | 7 | 31
75 | LIFT | CAR TOP | CONDITION OF CAR DOOR OPERATOR | 1. Door operator shall have free movement~ 2. All moving parts should be clean, lubricated and have free movement.~ 3. Car door lock mechanism (If provided) functional~ 4. Door drive belt / rope should be in good condition without any damages | 3~4~4~3 | Y~Y~Y~N | Car door air cord rope is rusted~Car door air cord rope found damaged~Car door drive belt is damaged~Car door mechanical lock found de-activated & not working | Y~Y~Y~N | 0.5 | 0.5 | 0.125~0.125~0.125~0.125 | 0.125~0.125~0.125~0.125 | 0 | 0 | A | 1 | [value-18] | 4 | 0
76 | LIFT | CAR TOP | CAR DOOR CONTACT(SWITCH) OPERATION | 1. Car door contact should be activated at <15 mm before the final closin in Center Opening doors. ~ 2. In Telescopinc door, contact should activate at 10 mm before final closing~ 3. There shall sufficient contact pressure~ 4. The contact may be provided on only one panel (rapid panel in case of telescopic doors) if the interconnecting mechanism of door panels is so arranged. | 3~5~3~4~3~3~3 | Y~Y~Y~Y~N~N~N | Switch is activating at far advance to 15 mm, prior to full close~Car door contact found bypassed~Cardoor switch cover is missing / damaged~Door contact found damaged~ Excess contact pressure~Poor contact pressure~Switch is not earthed | N~Y~N~N~N~N~N | 0.5 | 0.5 | 0.083~0.083~0.083~0.083~0.083~0.083 | 0.083~0.083~0.083~0.083~0.083~0.083 | 0 | 0 | A | 1 | [value-18] | 7 | 32
77 | LIFT | CAR TOP | SAFETY GEAR LINKS CONDITION | 1. All safety gear mechanism & linkage should be clean, lubricated & with free movement | 3~4 | Y~Y | Safety links & joints are not clean/ not lubricated~Missing check nuts/split pins in safety rods | Y~Y | 0.5 | 0.5 | 0.166~0.166~0.166 | 0.166~0.166~0.166 | 0 | 0 | M | 1 | [value-18] | 2 | 0
78 | LIFT | CAR TOP | CAR GUIDE SHOE & LINERS | 1. Guide shoe should have no play at the same time no excess pressure with the guide rails~ 2. Liners should be in good condition. No damages / in wornout condition~ 3. Guide shoes should be clean & in lubricated condition~ 4. Roller guides top should be guarded from falling objects | 3~3~3~4~3~4~3~3~3~3~3 | Y~N~Y~Y~Y~Y~Y~Y~N~N~Y | Guide shoes are not clean~Guide shoe play is excess~Guide shoe liners found wornout~Guide shoe liners found damaged / missing~Guide shoe play adjusting bolt is missing~ Roller guide tyre found damaged~Guide shoe assembly should be cleaned~ Roller guides top guard is missing~Roller guides tension is uneven/excess play~Roller guides are noisy~Roller guides tension spring found damaged | Y~N~Y~Y~Y~Y~Y~Y~N~N~Y | 0.5 | 0.5 | 0.045~0.045~0.045~0.045~0.045~0.045~0.045~0.045~0.045~0.045~0.045 | 0.045~0.045~0.045~0.045~0.045~0.045~0.045~0.045~0.045~0.045~0.045 | 0 | 0 | M | 1 | [value-18] | 11 | 0
79 | LIFT | CAR TOP | CWT GUIDE SHOE & LINERS | 1. Guide shoe should have no play at the same time no excess pressure with the guide rails~ 2. Liners should be in good condition. No damages / in wornout condition~ 3. Guide shoes should be clean & in lubricated condition~ 4. Roller guides top should be guarded from falling objects | 3~3~3~4~4~3~3~3~3 | Y~N~Y~Y~Y~Y~Y~N~N | Guide shoes are not clean~Guide shoe play is excess~Guide shoe liners found wornout~Guide shoe liners found damaged / missing~ Roller guide tyre found damaged~Guide shoe assembly should be cleaned~ Roller guides top guard is missing~Roller guides tension is uneven/excess play~Roller guides are noisy | Y~N~Y~Y~Y~Y~Y~N~N | 0 | 0 | 0~0~0~0~0~0~0~0 | 0~0~0~0~0~0~0~0 | 0 | 0 | M | 1 | [value-18] | 9 | 0
80 | LIFT | CAR TOP | CONDITION OF CAR TOP OILERS | Oilers should be clean & oil level should be maintained | 3~3~3~3~0 | Y~Y~Y~N~N | Oil level is poor in oilers~Oilers found damaged~Oilers are empty~Recommended to install auto oilers~Lubrication is not applicable, Roller guides provided | Y~Y~Y~N~N | 0.5 | 0.5 | 0.1~0.1~0.1~0.1~0.1 | 0.1~0.1~0.1~0.1~0.1 | 0 | 0 | M | 0 | [value-18] | 5 | 0
81 | LIFT | CAR TOP | LUBRICATION & CONDITION OF CAR GUIDE RAILS | 1. Guide rails should be clean and lubricated~ 2. Rail clips and joints should be intact | 3~3~3~3~0 | Y~Y~Y~Y~N | Guide rail are dry and not lubricated~Guide rails are not clean~Guide rails found rusted~Guide rails found with sludge~Lubrication is not applicable, Roller guides provided | Y~Y~Y~Y~N | 0.5 | 0.5 | 0.1~0.1~0.1~0.1~0.1 | 0.1~0.1~0.1~0.1~0.1 | 0 | 0 | M | 0 | [value-18] | 5 | 0
82 | LIFT | CAR TOP | CONDITION OF CWT TOP OILERS | Oilers should be clean & oil level should be maintained | 3~3~3~3~0 | Y~Y~Y~N~N | Oil level is poor in oilers~Oilers found damaged~Oilers are empty~Recommended to install auto oilers~Lubrication is not applicable, Roller guides provided | Y~Y~Y~N~N | 0.5 | 0.5 | 0.1~0.1~0.1~0.1~0.1 | 0.1~0.1~0.1~0.1~0.1 | 0 | 0 | M | 0 | [value-18] | 5 | 0
83 | LIFT | CAR TOP | LUBRICATION & CONDITION OF CWT GUIDE RAILS | 1. Guide rails should be clean and lubricated~ 2. Rail clips and joints should be intact | 3~3~3~3~0 | Y~Y~Y~Y~N | Guide rail are dry, should be lubricated~Guide rails need to be cleaned~Guide rails found rusted~Guide rails found with sludge~Lubrication is not applicable, Roller guides provided | Y~Y~Y~Y~N | 0.5 | 0.5 | 0.1~0.1~0.1~0.1~0.1 | 0.1~0.1~0.1~0.1~0.1 | 0 | 0 | M | 0 | [value-18] | 5 | 0
84 | LIFT | MACHINE ROOM | SAFE ACCESS | There shall be an easy access from the top landing to the lift machine room | 3~3~0~3~3 | Y~N~N~Y~N | Step over bridge is not provided on access way to machine room~Handrail is not provided on access stairs of machine room~Not Applicable - MRL elevators~Low overhead on the access way. Appropriate warning and protection is not provided~Uneven step heights in the staircase should be rectified or highlighted | Y~N~N~Y~N | 1 | 1 | 0.2~0.2~0.2~0.2~0.2 | 0.2~0.2~0.2~0.2~0.2 | 0 | 1 | M | 0 | [value-18] | 5 | 36
85 | LIFT | MACHINE ROOM | ACCESS LIGHT & WARNING STICKERS | 1. A notice bearing the following minimum inscription: Lift Machinery " DANGER. Access forbidden to unauthorized persons", &Danger 440 Volt- board with skeleton symbol also should be provided.~ 2. Access light with switch control outside the lift room should be provided | 3~3~3~3~3~3 | Y~N~Y~Y~Y~Y | Access light & switch control is not provided~Access light control switch is not available at outside the machine room~Warning instructions & Danger sign is not provided at machine room entrance/ door~Machine room is not identified~Access light is not working.~Warning instructions / Danger sign is faded | Y~N~Y~Y~Y~Y | 1 | 1 | 0.1~0.1~0.1~0.1~0.1~0.1~0.1~0.1~0.1~0.1 | 0.1~0.1~0.1~0.1~0.1~0.1~0.1~0.1~0.1~0.1 | 0 | 0 | M | 1 | [value-18] | 6 | 0
86 | LIFT | MACHINE ROOM | LOCKABLE DOOR | Locking arrangement shall be provided and lift machine room shall be kept locked | 3~3~3~3 | Y~Y~Y~Y | Machine room door is not locked~Locking arrangement is missing~Rain water protection is not provided~Door found rusted /damaged | Y~Y~Y~Y | 1 | 1 | 0.2~0.2~0.2~0.2~0.2 | 0.2~0.2~0.2~0.2~0.2 | 0 | 0 | M | 1 | [value-18] | 4 | 0
87 | LIFT | MACHINE ROOM | LIGHTING OF MACHINE ROOM | Adequate number of light points shall be provided and maintained in working order. | 3~3 | N~Y | Lighting is poor~Fused/ defective lights found | N~Y | 1 | 1 | 0.5~0.5 | 0.5~0.5 | 0 | 0 | M | 1 | [value-18] | 2 | 47
88 | LIFT | MACHINE ROOM | IDENTIFICATION OF EQUIPMENTS | 1. When there are more than one lift in a machine room, identification of all equipment is mandatory~ 2. Identification should be inline with common nomenclature | 4~4 | Y~Y | Identification is not inline with common nomenclature~Identification is missing in all equipments | Y~Y | 1 | 1 | 0.5~0.5 | 0.5~0.5 | 0 | 0 | M | 1 | [value-18] | 2 | 39
89 | LIFT | MACHINE ROOM | POWER MAIN SWITCH CONDITION | 1. Switch should be in correct rating~ 2. Mechanical operation of ON & OFF should be intact~ 3. LOTO facility should available.~ 4. Identification is mandatory when there are more than one lift in a machine room | 4~4~4~4~3 | N~Y~Y~Y~N | Switch lever is inactive~Switch lever found damaged~Switch lever is missing~Missing identification on 3 Phase / 1 Phase power mains~LOTO provision is not available | Y~Y~Y~N~N | 1 | 1 | 0.25~0.25~0.25~0.25 | 0.25~0.25~0.25~0.25 | 0 | 1 | M | 1 | [value-18] | 5 | 37
90 | LIFT | MACHINE ROOM | ACCESSIBILITY OF POWER MAIN SWITCHES | 1. Power mains should be at accessible height~ 2. When provided at higher places, permanent access ladder should be made available | 3~3 | Y~N | Not accessible. Provided above false ceiling~Not in the vicinity of lift | Y~N | 1 | 1 | 0.33~0.33~0.33 | 0.33~0.33~0.33 | 0 | 1 | M | 1 | [value-18] | 2 | 0
91 | LIFT | MACHINE ROOM | TRAP DOOR / HOISTING HOOKS CONDITION | 1. Hoist hook should be provided with valid test certificate or warning tag~ 2. Trap door should be painted with warning stripes~ 3. Trap door should be properly closed and no gaps on the floor | 4~3~3~3~3~0~0 | Y~Y~Y~Y~Y~N~N | Trap door is not closed properly~Trap door is not painted with warning stripes~Hooks/ beams certificate validity is expired~Hoist Hooks / beams are not painted~Valid test certificate or warning tag not provided on hoist hooks/ beams~Trap door is not applicable, MRL elevator~Trap door is not provided, Not applicable (MR) | Y~Y~Y~Y~Y~N~N | 1 | 1 | 0.2~0.2~0.2~0.2~0.2 | 0.2~0.2~0.2~0.2~0.2 | 0 | 1 | M | 0 | [value-18] | 7 | 0
92 | LIFT | MACHINE ROOM | EQUIPMENTS EARTHING AS PER STANDARD | 1. There should be two independent earth available from the sources. 2.Earthing main switches, lift motor, all tyes of control panel, Over Speed Governor switch, etc.~ 3. All medium voltage equipment shall be earthed by two separate and distinct connections with earth | 5~4~4~3~4~4~4~4 | Y~Y~Y~N~Y~N~N~N | Incoming main earth is not available~3 Phase equipments are not double earthed~Incoming earth is single. Two earth should be provided from different earth pits~Multiple earth wires provided in single bolt & no discrete connections~Earthing found with loose connections ~Governor is not earthed~Machine is not earthed~Controller is not earthed | Y~N~N~N~N~N~Y~Y | 1 | 1 | 0.125~0.125~0.125~0.125~0.125~0.125~0.125~0.125 | 0.125~0.125~0.125~0.125~0.125~0.125~0.125~0.125 | 0 | 1 | M | 1 | [value-18] | 8 | 38
93 | LIFT | MACHINE ROOM | MACHINE SHEAVE AND ROPE CONDITION | 1. There shall not be any uneven wearing and all the grooves should be in same level~ 2. The condition of grooves shall be such that the rope does not move when the traction sheave stops.~ 3. It shall not be possible to raise the empty car when the counterweight rested on buffer. ~ 4. Sheave & grooves with ropes should be in clean condition and free from sludge, excess oil & dust over it | 4~4~3~4~4~3~3~3~4~4~4 | Y~N~Y~Y~Y~Y~N~Y~Y~Y~Y | Sheave groove no. ---- from machine side is worn-out~Hoist ropes tension is not even~Hoist ropes are not cleaned and lubricated~Hoist ropes no. --- found worn-out ~ Hoist ropes found dry/rusted ~ Split pins are missing in thimble rod~Thimble rod check nut found loose~Hoist belts are not clean~Hoist belt no. --- found damaged near ---floor~Hoist ropes no. --- found damaged near ---floor~Metal powder protruding from drive sheave/ Ropes | Y~N~N~Y~N~N~N~N~Y~Y~N | 1 | 1 | 0.091~0.091~0.091~0.091~0.091~0.091~0.091~0.091~0.091~0.091~0.091 | 0.091~0.091~0.091~0.091~0.091~0.091~0.091~0.091~0.091~0.091~0.091 | 0 | 0 | M | 1 | [value-18] | 11 | 40
94 | LIFT | MACHINE ROOM | CONDITION OF MACHINE MOUNTING & ISOLATION | 1. Mounting & upthrust bolts should be intact~ 2. Isolation rubber should not be overcompressed and no damages~ 3. Upthrust bolt should not bypass the rubber isolation | 3~3~3~3~3 | Y~Y~N~N~Y | Rubber pad found damaged~Rubber pad found compressed~Upthrust bolt gap is more.~Upthrust bolt check nut is loose~Upthrust bolt is missing | Y~Y~N~N~Y | 1 | 1 | 0.167~0.167~0.167~0.167~0.167~0.167 | 0.167~0.167~0.167~0.167~0.167~0.167 | 0 | 0 | M | 1 | [value-18] | 5 | 0
95 | LIFT | MACHINE ROOM | ANY ABNORMAL NOISE IN MACHINE | There shall not be any abnormal noise in the machine & motor | 3~3~3 | N~N~N | Machine operation is noisy~Motor operation is noisy~Encoder operation is noisy | Y~Y~N | 1 | 1 | 0.2~0.2~0.2~0.2~0.2 | 0.2~0.2~0.2~0.2~0.2 | 0 | 0 | M | 1 | [value-18] | 3 | 41
96 | LIFT | MACHINE ROOM | ANY ABNORMAL HEAT IN MACHINE | There shall not be any abnormal heat in the machine & motor | 3~3 | N~N | Abnormal Motor heat detected~Abnormal machine heat detected | Y~N | 1 | 1 | 0.05~0.05~0.05~0.05~0.05~0.05~0.05~0.05~0.05~0.05 | 0.05~0.05~0.05~0.05~0.05~0.05~0.05~0.05~0.05~0.05 | 0 | 0 | A | 1 | [value-18] | 2 | 42
97 | LIFT | MACHINE ROOM | CONDITION OF LUBRICATION & OIL LEAKAGE | 1. No oil leak from the gear box or at any part of the machine~ 2. Gear oil level should be intact. Oil should circulate when in operation.~ 3. Oil level should be moving down in the level monitor when in operation~ 4. Oil viscosity should be verified and needs to replace periodically | 3~3~3~3~0 | Y~Y~Y~N~N | Oil leak found in machine~Oil level is poor~Oil level is excess~Gear oil is old and found thick~Not applicable -Gearless machine | Y~Y~Y~N~N | 1 | 1 | 0.250~0.250~0.250~0.250 | 0.250~0.250~0.250~0.250 | 0 | 0 | M | 0 | [value-18] | 5 | 0
98 | LIFT | MACHINE ROOM | CONDITION OF MAIN & ARD CONTROLLER | 1. Main & ARD controller should have an easy access and doors to open/ close with lock~ 2. Battery terminals should be well guarded & seccured from accidental physical contact~ 3. Contacts operation should be without vibration and chattering~ 4. Wiring should be neatly bunched and routed~ 5. Controllers fixing should be rigid~ 6. Controllers should be in clean condition | 3~3~3~3~3~3~3~3~3~3 | Y~N~N~N~Y~Y~N~Y~Y~Y | ARD Battery terminals are not guarded~ARD Controller is shaky~Unable to access/open ARD controller door~Main Controller is shaky~Controller is not clean~Controller contactors are hanging~Contactors are noisy~ Controller wiring is not routed and not secured~ARD, Controller are single earthed, should be double~Controller light is not working | Y~N~N~N~Y~Y~N~Y~Y~Y | 1 | 1 | 0.077~0.077~0.077~0.077~0.077~0.077~0.077~0.077~0.077~0.077~0.077~0.077~0.077 | 0.077~0.077~0.077~0.077~0.077~0.077~0.077~0.077~0.077~0.077~0.077~0.077~0.077 | 0 | 0 | M | 1 | [value-18] | 10 | 0
99 | LIFT | MACHINE ROOM | LOG CARD ENTRY & HISTORY | 1. Log book should be kept and maintained regulalry~ 2. All events of maintenance, breakdowns, repair & replacement of parts should be recorded in the log book | 3~3 | Y~N | Log book is not updated~Log book is not provided | Y~N | 1 | 1 | 0.333~0.333~0.333 | 0.333~0.333~0.333 | 0 | 0 | M | 1 | [value-18] | 2 | 0
100 | LIFT | MACHINE ROOM | VENTILATION OF THE MACHINE ROOM | 1. There shall be adequate cross ventilation preferably with exhaust fan.or Sufficient A/C should be provided~ 2. Ambient temperature of the machine room sshould be maintained | 3~3~3~3~3~3~3~0 | N~Y~Y~Y~N~Y~Y~N | A/C is not working~Cross ventilation is not provided~Exhaust fan is not working~Exhaust fan is missing~Machine room temperature is high~Ventilation louvers found broken~Exhaust fan is not guarded~Not Applicable, MRL elevator | N~Y~Y~Y~N~Y~Y~N | 1 | 1 | 0.125~0.125~0.125~0.125~0.125~0.125~0.125~0.125 | 0.125~0.125~0.125~0.125~0.125~0.125~0.125~0.125 | 0 | 1 | M | 0 | [value-18] | 8 | 0
101 | LIFT | MACHINE ROOM | GOVERNOR & ROPE CONDITION | 1. Governor pulley should be in plumb (Verticality)~ 2. Mounting should be rigid~ 3. Sheave grooves & rope should be in clean condition~ 4. No rust, damages in governor ropes~ 5. Governor ropes should not be rubbing with governor base or floor slab | 4~3~3~3~4~3~3~3~4~4~4~4 | Y~Y~Y~Y~Y~Y~Y~Y~N~Y~N~N | Governor pulley is not in plumb~Down direction mark is not provided~Governor rope is not clean~Governor rope is bend at --- floor~Governor rope found damaged at --- floor~Governor rope is rusted~Governor accessories are not clean and not lubricated~Governor guard is missing~Governor operation is noisy~Governor rope is rubbing with the slab hole/ base~Governor remote access is not working (MRL)~Governor remote access is not provided (MRL) | Y~Y~Y~Y~Y~Y~Y~Y~N~Y~N~N | 2 | 2 | 0.2~0.2~0.2~0.2~0.2~0.2~0.2~0.2~0.2~0.2~0.2~0.2~0.2 | 0.2~0.2~0.2~0.2~0.2~0.2~0.2~0.2~0.2~0.2~0.2~0.2~0.2 | 0 | 0 | M | 1 | [value-18] | 12 | 0
102 | LIFT | MACHINE ROOM | OPERATION OF GOVERNOR & SAFETY GEAR | 1. Safety gear should be engaged when the speed governor is activated~ 2. Once the safety gear is activated, downward movement of car should not be possible. 3. The force applied on governor rope should be sufficient to lift the safety rods. 4. Force mentioned on governor data, shall be inline or more than the force mentioned in safety ghear | 5~5~5 | N~N~N | Governor is not locking the rope~Safety gear mechanism is not activating~ Safety gear is activated partially and the car is moving further | Y~Y~Y | 1 | 1 | 0.05~0.05~0.05~0.05~0.05~0.05~0.05~0.05~0.05~0.05 | 0.05~0.05~0.05~0.05~0.05~0.05~0.05~0.05~0.05~0.05 | 0 | 0 | M | 1 | [value-18] | 3 | 43
103 | LIFT | MACHINE ROOM | FUNCTIONAL GOVERNOR OVERSPEED SWITCH | 1. Governor overspeed switch should be functional(if provided)~ 2. There shall be no damages in the switch | 5~3~2 | N~Y~Y | Governor overspeed switch is not working~Governor overspeed switch found damaged~Not provided, recommended | Y~N~N | 1 | 1 | 0.05~0.05~0.05~0.05~0.05~0.05~0.05~0.05~0.05~0.05 | 0.05~0.05~0.05~0.05~0.05~0.05~0.05~0.05~0.05~0.05 | 0 | 0 | M | 1 | [value-18] | 3 | 44
| LIFT | MACHINE ROOM | FLOOR LEVEL MARKINGS ON HOIST ROPES/AVAILABILITY OF FLOOR LEVEL REFERENCE | 1. Floor level marking should be available on hoist ropes to enable manual rescue 2. Floor level reference should be available by means of indicator / buzzer 3. This buzzer should be in working condition even when the elevator power is OFF 4. In MRL where ropes marking is not possible and hence buzzer / indocator is mandatory | 3~3~3 | Y~Y~N | Floor level marking is not avilable, should be provided~Floor level markings are faded, to be re-painted~ Floor leveL buzzer/ indicator is not working, to be rectified | N~N~Y | [5 empty] | 0 |  | 1 | tyu4567kjhg | 3 | 0
104 | LIFT | MACHINE ROOM | MANUAL RESCUE OPERATION | 1. Brake releasing device can be Manual & Battery Operated as applicable~ 2.Manual rescue device should be in operatable condition to perform the rescue | 5~5 | N~N | Not working~ Unable to check, device is not available | Y~Y | 0 | 0 | 0 | 0 | 1 | 0 | M | 1 | [value-18] | 2 | 45
105 | LIFT | MACHINE ROOM | MANUAL BRAKE RELEASE DEVICE | 1. Rescue device should be placed in designated place 2. Brake releasing device can be Manual & Battery Operated as applicable~ 3. When there are multiple units in one m/c room, atleast one device should be available for each type of machine | 3~3 | Y~N | Rescue Device not kept in right place~Single device only provided for multiple units | Y~N | 2 | 2 | 2~0.67~0.67~0.67 | 2~0.67~0.67~0.67 | 0 | 0 | M | 1 | [value-18] | 2 | 0
106 | LIFT | MACHINE ROOM | MANUAL BRAKE RELEASE INSTRUCTIONS | 1. Manual rescue instructions should be provided with suitable illustrations~ 2. Instructions should be inline with type of brake mechanism& machine~ 3. Instructions should be available also in local language | 4~4~3 | N~Y~Y | Rescue Instructions are not provided~Rescue Instructions are not inline with the type of machine~Rescue Instructions are faded | Y~Y~Y | 1 | 1 | 0.05~0.05~0.05~0.05~0.05~0.05~0.05~0.05~0.05~0.05 | 0.05~0.05~0.05~0.05~0.05~0.05~0.05~0.05~0.05~0.05 | 0 | 0 | M | 1 | [value-18] | 3 | 46
107 | LIFT | MACHINE ROOM | BRAKE OPERATION & CONDITION | 1. All moving parts of the brake shall be with free movement, lubricated necessarily and should be verified by manual operation.~ 2. There shall no be abnormal noise during the operation~ 3. Brake liners are not wornout & should be good condition | 3~3~4~3~4 | N~N~Y~Y~Y | Brake operation is noisy.~All moving parts of the brake is not clean and not lubricated~Brake liners are wornout~Brake (feed back) switch cover is missing~Brake (feed back) switch is not in circuit | N~N~Y~Y~Y | 1 | 1 | 0.250~0.250~0.250~0.250 | 0.250~0.250~0.250~0.250 | 0 | 0 | M | 1 | [value-18] | 5 | 0
108 | LIFT | MACHINE ROOM | SLAB HOLE CUT OUTS FOR ROPES | 1. Slab hole should not be excess in size than the required.~ 2. Riser should be provided to avoid falling objects in to the shaft~ 3. Slab holes should not touch/ rub with the ropes | 3~3 | Y~Y | Slab cutouts are excess in size~Upstand is not provided on slab cutouts | Y~Y | 1 | 1 | 0.5~0.5 | 0.5~0.5 | 0 | 0 | M | 1 | [value-18] | 2 | 0
109 | LIFT | MACHINE ROOM | GUARDING OF ALL ROTATING PARTS | Effective protection/ guarding shall be provided for all accessible rotating/ moving parts, which may be dangerous | 4~4~3~3~4 | Y~Y~Y~Y~Y | Drive sheave & ropes are not guarded~Hoist ropes are not guarded~Exhaust fan is not guarded~Governor assembly is not guarded~All rotating parts are not guarded | Y~Y~Y~Y~Y | 1 | 1 | 0.143~0.143~0.143~0.143~0.143~0.143~0.143 | 0.143~0.143~0.143~0.143~0.143~0.143~0.143 | 0 | 0 | M | 1 | [value-18] | 5 | 0
110 | LIFT | MACHINE ROOM | SMOKE DETECTOR / FIRE EXTINGUISHER | 1. Machine room shall be provided with Fire detectors & extinguishers, with a high operating temperature, appropriate for the electrical equipment, stable over a period of time, and suitably protected against accidental impact~ 2. Fire extinguishers should be tested/ refilled periodically and the expiry date should be available on the unit | 3~4~4 | N~Y~N | Smoke detector is not working~Fire extinguisher refilling due date is expired~Fire extinguisher is not provided | N~Y~N | 1 | 1 | 0.2~0.2~0.2~0.2~0.2 | 0.2~0.2~0.2~0.2~0.2 | 0 | 1 | M | 0 | [value-18] | 3 | 0
111 | LIFT | MACHINE ROOM | GENERAL CONDITION OF MACHINE ROOM | 1. Machine room should be clean from dust, oil spill and water.~ 2. It should not be used as a storage place for any other purpose~ 3. Access for other purpose should not be given through lift room~ 4. Room should be painted with sufficient lighting~ 5. All trunking, cabling, wirings should be neatly routed and secured~ 6. No uneven surfaces in the macine room~ 7. Should be protected from rain water entry | 3~3~3~3~3~3 | N~Y~Y~Y~Y~Y | Machine room is not clean~Unwanted materials found in machine room~Machine room is used by other pruposes~A/C water is leaking in the machine room~Missing trough covers in the machine room~Trough covers are not in place | N~Y~Y~Y~Y~Y | 1 | 1 | 0.11~0.11~0.11~0.11~0.11~0.11~0.11~0.11~0.11 | 0.11~0.11~0.11~0.11~0.11~0.11~0.11~0.11~0.11 | 0 | 0 | M | 1 | [value-18] | 6 | 0
112 | LIFT | MACHINE ROOM | FUNCTIONAL STOP SWITCHES MCR (IF APPLICABLE) | Where there are two different level(Split) in MCR and the height difference is more than 500 mm, additional STOP switch should be provided near machine. | 0~4~3~4 | N~N~Y~N | Not applicable~STOP switch is not functional~STOP switch found damaged~STOP switch is not provided(Split level MCR) | N~N~Y~N | 1 | 1 | 0.05~0.05~0.05~0.05~0.05~0.05~0.05~0.05~0.05~0.05 | 0.05~0.05~0.05~0.05~0.05~0.05~0.05~0.05~0.05~0.05 | 0 | 0 | M | 1 | [value-18] | 4 | 48
113 | LIFT | MACHINE ROOM | FUNCTIONAL CONTROLLER INSPECTION SWITCHES | If provided, all the features should be functional | 0~3~3~4~3~3 | N~N~N~N~Y~Y | Not applicable~Up direction switch/ button is not working~Down direction switch/ button is not working~INSPECTION/NORMAL switch is not working~INSPECTION/NORMAL switch found damaged~Direction button/s found damaged | N~N~N~N~N~N | 1 | 1 | 0.05~0.05~0.05~0.05~0.05~0.05~0.05~0.05~0.05~0.05 | 0.05~0.05~0.05~0.05~0.05~0.05~0.05~0.05~0.05~0.05 | 0 | 0 | M | 1 | [value-18] | 6 | 49
114 | LIFT | FLOOR LANDING | FUNCTION OF UNLOCKING DEVICE | De locking arrangement shall be provided at every landing | 3~4~4~3 | N~Y~N~N | Mechanically hard to operate~Device is missing~Not working at--- floor~Not accessible | N~Y~Y~N | 1 | 1 | 0.33~0.33~0.33 | 0.33~0.33~0.33 | 0 | 0 | M | 1 | [value-18] | 4 | 21
115 | LIFT | FLOOR LANDING | ACCESSIBILITY OF UNLOCKING DEVICE | 1. The position of the unlocking triangle shall not exceed 2.00 m in height above the landing~ 2. Suitable key should be available to access the device if the height is exceeding | 3 | Y | Device is not at accessible, provided at the height of ---mm | Y | 1 | 1 | 0.5~0.5 | 0.5~0.5 | 0 | 0 | M | 1 | [value-18] | 1 | 0
116 | LIFT | FLOOR LANDING | DOOR PANEL TO DOOR PANEL /JAMB GAP | 1. In closed condition, gap from door panel to side jamb, transom panel and to the sill shall not exceeed 6 mm | 4~3~3 | Y~Y~Y | Jamb Gap --- mm is exceeding the max. limit of 6 mm at --- floors~Entrance marble to Jamb Gap is more at --- floors~Jamb Gap --- mm is less than the minimum limit of 3 mm at --- floors | Y~Y~Y | 1 | 1 | 0.33~0.33~0.33 | 0.33~0.33~0.33 | 0 | 0 | A | 1 | [value-18] | 3 | 0
117 | LIFT | FLOOR LANDING | WHETHER THE DOORS ARE FULLY OPENING | Doors should open completely and the edges shall not be protruding from jamb | 3 | Y | Doors are not fully opening & projected outside at --- floors | Y | 1 | 1 | 0.5 | 0.5 | 0 | 0 | M | 1 | [value-18] | 1 | 0
118 | LIFT | FLOOR LANDING | CONDITION OF DOOR PANELS | 1. No scratches or dent on the panels.~ 2. In closed condition, door edges should be seated together evenly and without any gap~ 3. Mechanically door panels shall have free movement | 3~3~3~3~3 | Y~Y~Y~Y~N | Door panels found rusted at --- floors~Door dent at --- floors~ Door panel scratches at --- floors~Protective covers is not removed~ Panel found twisted/ mechanical friction at --- floors | Y~Y~Y~Y~N | 1 | 1 | 0.1~0.1~0.1~0.1~0.1 | 0.1~0.1~0.1~0.1~0.1 | 0 | 0 | M | 1 | [value-18] | 5 | 0
119 | LIFT | FLOOR LANDING | FUNCTION OF HALL BUTTON | 1. Hall button assembly should be at accessible height and rigid in fixing~ 2. Direction arrow should be visible on buttons~ 3. Call register light should be working when the button is pressed~ 4. Braille markings should be available where applicable~ 5. No damages should be seen in the buttons & assy.~ 6. In DCS, Elevator location direction should be clearly indicated | 3~3~3~3~3 | N~Y~Y~N~Y | Non functional hall buttons at --- floors~ Damaged hall buttons at --- floors~ Missing Braille markings at --- floors~ Hall button fixing is shaky & not rigid at --- floors~ Damaged hall fixtures at ---floors | N~Y~N~N~Y | 1 | 1 | 0.14~0.14~0.14~0.14~0.14~0.14~0.14 | 0.14~0.14~0.14~0.14~0.14~0.14~0.14 | 0 | 0 | M | 1 | [value-18] | 5 | 11
120 | LIFT | FLOOR LANDING | FUNCTION OF DCS | If DCS is provided, all features should be functional | 0~3~3~3~3~2 | N~Y~Y~Y~Y~N | Not applicable, non DCS elevator~ Non functional DCS pads at --- floors~ Damaged DCS pads at --- floors~ Allocated Elevator no. & actual elevator No. is mismatching~ Allocated Elevator position shown in DCS pad is wrong~ Wheel chair feature is not working/ not provided | N~Y~Y~N~N~N | 1 | 1 | 0.05~0.05~0.05~0.05~0.05~0.05~0.05~0.05~0.05~0.05 | 0.05~0.05~0.05~0.05~0.05~0.05~0.05~0.05~0.05~0.05 | 0 | 0 | M | 1 | [value-18] | 6 | 14
121 | LIFT | FLOOR LANDING | FUNCTION OF HALL LANTERNS | 1. Rigid in fixing~ 2. Lanterns illumination should be clearly visible~ 3. No damages should be seen | 0~3~3 | N~N~Y | Not provided-Not applicable ~Hall lanterns are not working at --- floors~Damaged hall lanterns at --- floors | N~Y~Y | 1 | 1 | 0.013~0.013~0.013~0.013 | 0.013~0.013~0.013~0.013 | 0 | 0 | M | 0 | [value-18] | 3 | 13
122 | LIFT | FLOOR LANDING | FUNCTION OF HALL POSITION DISPLAY | 1. Display should be clearly visible~ 2. Fixing should be rigid~ 3. No damages should be seen | 4~3~3~3 | Y~Y~N~Y | Floor number is showing wrongly~Display is not working at --- floors~Time display is malfunctioning at --- floors~Display found damaged at --- floors | N~Y~N~Y | 1 | 1 | 0.14~0.14~0.14~0.14~0.14~0.14~0.14 | 0.14~0.14~0.14~0.14~0.14~0.14~0.14 | 0 | 0 | M | 1 | [value-18] | 4 | 12
123 | LIFT | FLOOR LANDING | FIREMAN OPERATION | 1. In Fire Return mode, lift should be grounded at designated floor and doors should remain in open position~ 2. Elevator should go in shutdown mode with doors open & cabin lights in OFF condition~ 3. In fireman mode, lift should available in door open condition with cabin lights are on ON condition. ~ 4. Door operation should be under manual control~ 5. Only one desired car call should be registered~ 6. Hall calls shall not be registered/ responded | 4~4 | N~N | Not working~Not provided | Y~Y | 3 | 3 | 3~0~3~0.38~0.38~0.38~0.38~0.38~0.38~0.38~0.38 | 3~0~3~0.38~0.38~0.38~0.38~0.38~0.38~0.38~0.38 | 1 | 0 | M | 1 | [value-18] | 2 | 20
124 | LIFT | FLOOR LANDING | FIREMAN OTHER DETAILS | 1. Elevator should return to the floor where fireman switch/ access is provided~ 2. Fireman switch should be covered by glass panel with identification~ 3. A device/ tool should be available near the vicinity of fireman sw. to break the glass during emergency 4. Fireman lift should be clearly identified | 4~4~3~3~3~0 | N~N~Y~Y~N~N | Lift grounding at wrong floor~All lifts are fire emergency return only, fireman lift is not available~Fireman switch glass is missing~Fireman switch glass found broken~Doors safety sensor is not bypassing in fireman mode~Fireman switch is not provided, working through BMS (Information) | N~N~Y~Y~N~N | 0 | 0 | 0~0~0~0~0 | 0~0~0~0~0 | 0 | 0 | M | 1 | [value-18] | 6 | 0
125 | LIFT | FLOOR LANDING | FIREMAN AUDIO & VISUAL INDICATOR | 1. There should be an audio or voice announcement when fireman signal is triggered~ 2. A visual display should be working when fireman signal is triggered | 3~3~3 | N~N~N | Fireman audio &Visual indicator is not working, recommended ~Fireman audio is not working,recommended~Fireman visual indicator is not working,recommended | N~N~N | 0 | 0 | 0~0~0 | 0~0~0 | 0 | 0 | M | 1 | [value-18] | 3 | 0